## Slide 1: Introduction to NRW
Introduction to IWA Water Balance, NRW components and Performance indicators

## Slide 2: Content
IWA Water Balance
NRW components
NRW Target Level
Summary

## Slide 3: IWA Water Balance

## Slide 4: What is Non-Revenue Water (NRW)?
NRW is the volume of water supplied into the network that does not generate sales revenue
$
Revenue
Non-Revenue Water
$
X

## Slide 5
Illegal connections
Meter inaccuracy
Real losses
Apparent Losses
Non-Revenue Water
Notes: 5

## Slide 6
Typical losses from a water supply system
Notes: 6

## Slide 7: IWA Water balance
2 oktober 2018
7
Total System Input Volume | Authorised consumption | Billed authorised consumption | Billed metered consumption | Revenue water
 |  |  | Billed unmetered consumption | 
 |  | Unbilled authorised consumption | Unbilled metered consumption | Non-revenue water
 |  |  | Unbilled unmetered consumption | 
 | Water losses (Unaccounted-For Water) | Apparent losses (Commercial losses) | Unauthorised consumption | 
 |  |  | Metering inaccuracies and data errors | 
 |  | Real losses (Physical losses) | Leakage in transmission and distribution lines | 
 |  |  | Leakage and overflows at storage tanks | 
 |  |  | Leakage on service connections up to customer meters | 
Notes: 7

## Slide 8: IWA Water balance
2 oktober 2018
8
Total System Input Volume | Authorised consumption | Billed authorised consumption | Paid billed metered consumption | Revenue water
 |  |  | Paid billed unmetered consumption | 
 |  |  | Unpaid billed metered consumption | Non-revenue water
 |  |  | Unpaid billed unmetered consumption | 
 |  | Unbilled authorised consumption | Unbilled metered consumption | 
 |  |  | Unbilled unmetered consumption | 
 | Water losses (UFW) | Apparent losses (Commercial losses) | Unauthorised consumption | 
 |  |  | Metering inaccuracies and data errors | 
 |  | Real losses (Physical losses) | Leakage in transmission and distribution lines | 
 |  |  | Leakage and overflows at storage tanks | 
 |  |  | Leakage on service connections | 
Taking into account the billing and collection efficiency
Notes: 8

## Slide 9: Non-Revenue Water Metaphor
A quote of a concerned Managing Director:
“Non-Revenue Water is like a disease. There are tons of known medicine (NRW reduction approaches) for our disease called NRW and we have tried to applied some medicine. However it seems that tried medicine is not curing our disease. The trials of using the medicine had cost us a lot of effort, money and hope. Therefore, before trying to apply a new medicine we need to first analyse our disease, only then we can know which medicines we need to apply to cure our disease, before our companies dies of the NRW”.

## Slide 10: NRW Components

## Slide 11: NRW Components in Each DMA
To allow for prioritisation of efforts to reduce NRW one needs to calculate/estimate the DMA’s water balance components
Using available data and experience, and extra on-site measurements, one can calculate/estimate the:
  Unbilled Authorised Consumption
  Commercial (apparent) loss components , and
  Physical (real) loss components
  Billing-Collection efficiency
Chart: 
Nrw components
11

## Slide 12
Reducing commercial losses directly generates revenue for the water company
Reducing physical losses:
  Reduces the cost of producing the water (less water needed, less chemical and energy use)
  Improves customer service (more pressure, less supply interruptions and less contamination)
Furthermore, improving the billing-collection efficiency will also improve the water utilities’ revenue
How would you prioritise NRW reduction?
NRW Components in Each DMA

## Slide 13: Unbilled Authorised Consumption

## Slide 14: Unbilled Authorised Consumption
What is Unbilled Authorised Consumption?
Water legitimately consumed but not billed
Cannot be reduced unless there is a change in policy
Still should be metered as part of the water balance
This can be:
  Water fountains
  Pipe and sewer flushing
  Watering parks and gardens / sprinklers
  Public drinking fountains
  Fire fighting – e.g. hydrants

## Slide 15: Commercial Losses

## Slide 16: Key Components of Commercial Loss
Unauthorised Consumption | Legitimate connections that were never entered into the billing system and are therefore never invoiced (intentional and accidental) Permanent or temporary meter bypass Illegal connections Illegal use of fire hydrants
Meter Inaccuracies | Volume under-recorded by revenue meter due to its condition Over-sized revenue meters Meter tampering (water theft)
Meter Reading Errors | Corruption meter readers (collusion with customers) Meter reading errors (mistakes, or unreadable meters)
Accounting Errors | Data handling errors billing department Bills sent to wrong address

## Slide 17: Four Approaches to Commercial Loss Reduction
Commercial Loss Reduction
Improve billing database
Meter maintenance
Meter reader awareness and training
Customer and local agencies’ awareness
Prioritise your Commercial Loss Approach

## Slide 18: Physical Losses (leakage)

## Slide 19: Physical Losses (leakage)
Leakage is the water escaping from the distribution network before reaching the customer
This is usually in the form of leaks from the:
Transfer and distribution pipes;
Joints and fittings including air valves, hydrants etc;
Service reservoir/storage tank floors and walls and overflows;
Service connections up to the point of customer boundary or meter

## Slide 20: Four Approaches to Leak Reduction
Leakage Reduction
Speed and Quality of Repairs
Pressure Management
Active Leakage Control
Pipe materials, installation, replacement and maintenance
Prioritise your Leak Reduction Approach

## Slide 21: NRW Target Level

## Slide 22: Target: Economic Level of Leakage
The Economic Level of Leakage (ELL) is ‘the level of leakage at which any further reduction would incur costs greater than the benefits derived from the savings’
In theory, the ELL would serve as the water company’s leakage level target
In practice, it is extremely difficult and time consuming to calculate the ELL; it is specific to each water company and even to each DMA
Consequently, best international practice for leakage target setting uses the easier performance indicators of:
  Infrastructure Leakage Index (ILI); and
  Volume of Leakage per Service Connection per Day
Calculating these leak performance indictors enables DMAs to be prioritised for proactive leak reduction activities

## Slide 23: Method 1 - Infrastructure Leakage Index
Infrastructure Leakage Index (ILI) is the ratio of:
It is the international indicator for water network efficiency
An ILI of 4 is comparable with an efficient water company
It can also be used to compare leakage performance across DMAs
‘Minimum Achievable Annual Physical Losses’ is calculated by:
Referred to as MAAPL – Minimum Achievable Annual Physical Losses
Referred to as CAPL – Current Annual Volume of Physical Losses
MAAPL (litres/day) = (18 x Lm + 0.8 x Nc + 25 x Lp) x P
Where Lm = mains length (km); Nc = number of service connections; Lp = total length of private pipe, property boundary to customer meter (km); and P = average pressure (m)
Actual Leakage
-----------------------------------------------------------
Minimum Achievable Leakage
Infrastructure Leakage Index =

## Slide 24: Measuring Customer Supply Pipe length
Estimate the average distance of pipe on customer property ‘D’ for the DMA
Lp is the sum of the pipe lengths from the property boundary to the customer meter

## Slide 25: Method 1 - Infrastructure Leakage Index
Example calculation for Minimum Achievable Leakage of a DMA:
DMA Data | Value | Units
Total length of pipe (Lm) | 4.81 | Km
Number of connections (Nc) | 1,196 | Number
Total Service connection length (Lp) | 3.6 (average D=3m) | Km
Average DMA pressure | 11.7 | Metre
Minimum Achievable Annual Volume of Physical Losses | 13.2* | m3 / day
*Minimum Achievable Leakage for DMA =
((18x 4.81 x11.7) + (0.8 x 1,196 x 11.7) + (25 x 3.6 x 11.7))/1000 = 13.2 m3/day
MAAPL (litres/day) = (18 x Lm + 0.8 x Nc + 25 x Lp) x P

## Slide 26: Method 1 - Infrastructure Leakage Index
Actual Leakage
----------------------
Minimum Achievable Leakage
ILI Range | Band | Leakage Reduction
< 4 | A | Further loss reduction may be uneconomical
4 to < 8 | B | Lower priority
8 to < 16 | C | Medium Priority
≥ 16 | D | High Priority
Evaluating the Infrastructure Leakage Index
Infrastructure Leakage Index =

## Slide 27: Method 1 - Infrastructure Leakage Index
Example evaluation Infrastructure Leakage Index
 | DMA 1 | DMA 2 | DMA 3 | DMA 4 | DMA 5 | DMA 6
Actual Leakage | 776 | 180 | 51 | 92 | 400 | 210
Minimum Possible Leakage | 13.2 | 14.9 | 17.1 | 16.4 | 11.4 | 14.6
ILI | 59 | 12 | 3 | 6 | 35 | 14
Category | D | C | A | B | D | C
ILI Range | Band | Leakage Reduction
< 4 | A | Further loss reduction may be uneconomical
4 to < 8 | B | Lower priority
8 to < 16 | C | Medium Priority
≥ 16 | D | High Priority

## Slide 28: Leakage Target Setting Using ILI
ILI Range | Band | Leakage Reduction
< 4 | A | Further loss reduction may be uneconomical
4 to < 8 | B | Lower priority
8 to < 16 | C | Medium Priority
≥ 16 | D | High Priority
 | DMA 1 | DMA 2 | DMA 3 | DMA 4 | DMA 5 | DMA 6
Actual Leakage | 776 | 180 | 51 | 92 | 400 | 210
Leak Reduction Volume | 700 | 90 | 0 | 0 | 330 | 120
Target leakage (m3/day) | 76 | 90 | 51 | 92 | 70 | 90
Minimum Possible Leakage | 13.2 | 14.9 | 17.1 | 16.4 | 11.4 | 14.6
ILI | 6 | 6 | 3 | 6 | 6 | 6
Category | B | B | A | B | B | B

## Slide 29: Method 2 – Leakage/Connection/Day
Evaluating the Leakage / Connection / Day
Misleading and imprecise indicator, particularly in systems with intermittent supply and very low operating pressures. Utilities with a lower percentage of NRW might be doing worse than a utility with a higher percentage of NRW. % may be used when comparing changes within one area when ‘outside factors’ (average supply time, pressure) do not change
%
m3/connection/day
Water Volume not Sold
Water Volume Produced
Water Volume not Sold/24h* supply
# connections
This unit IWA has set as the international standard performance indicator for NRW
* With intermittent supply, the daily volume lost has to be extrapolated. I.e. with 17 hours supply, multiply by 24/17

## Slide 30: Method 2 – Leakage/Connection/Day
Source: Water Supply and Sanitation Sector Board Discussion Paper Series, Paper No. 8, December 2006

## Slide 31: Method 2 – Leakage/Connection/Day
International NRW Assessment
Calculate NRW in m3/connection/day
Reference the performance category using the average DMA pressure
NRW Management Performance Category | NRW in litres/connection/day when the system is pressurised at an average DMA pressure of: |  |  |  | 
 | 10m | 20m | 30m | 40m | 50m
A1 | <55 | <80 | <105 | <130 | <155
A2 | 55-110 | 80-160 | 105-210 | 130-260 | 155-310
B | 110-220 | 160-320 | 210-420 | 260-520 | 310-620
C | 220-400 | 320-600 | 420-800 | 520-1000 | 620-1200
D | >400 | >600 | >800 | >1000 | >1200

## Slide 32: Method 2 – Leakage/Connection/Day
 | DMA 1 | DMA 2 | DMA 3 | DMA 4 | DMA 5 | DMA 6
Actual Leakage | 776 | 180 | 51 | 92 | 400 | 210
# of Connections | 1,196 | 1,515 | 1,603 | 1,652 | 1,298 | 1,573
Leakage / connection | 648 | 119 | 32 | 56 | 308 | 133
Category* | D | B | A1 | A2 | C | B
A1: World class NRW management performance; potential for further NRW reductions is small unless there is potential for pressure reduction or accuracy improvement of large customer meters
A2: Further NRW reduction may be uneconomic unless there are water shortages or very high water tariffs; a detailed water audit is required to identify cost-effective improvements
B: Potential for marked improvements; establish a water balance to quantify the components of NRW; consider pressure management, better active leakage control practices, and better network maintenance; improve customer meter management, review meter reading, data handling and billing processed and identify improvement potentials
C: Poor NRW record; tolerable only if water is plentiful and cheap; even then, analyze level and causes of NRW and intensify NRW reduction efforts
D: Highly inefficient; a comprehensive NRW reduction program is imperative and high-priority *Example at 10m pressure

## Slide 33: Method 2 - Leakage Target Setting Using L/C/D and Pressure
 | DMA 1 | DMA 2 | DMA 3 | DMA 4 | DMA 5 | DMA 6
Actual leakage | 776 | 180 | 51 | 92 | 400 | 210
Number of connections | 1,196 | 1,515 | 1,603 | 1,652 | 1,298 | 1,573
Target leakage (m3/day) | 700 | 90 | 0 | 0 | 334 | 117
Leakage after project | 76 | 90 | 51 | 92 | 66 | 93
Leakage / connection | 63 | 59 | 32 | 56 | 51 | 59
Category | A2 | A2 | A1 | A2 | A2 | A2
NRW Management Performance Category | NRW in litres/connection/day when the system is pressurised at an average DMA pressure of: |  |  |  | 
 | 10m | 20m | 30m | 40m | 50m
A1 | <55 | <80 | <105 | <130 | <155
A2 | 55-110 | 80-160 | 105-210 | 130-260 | 155-310
B | 110-220 | 160-320 | 210-420 | 260-520 | 310-620
C | 220-400 | 320-600 | 420-800 | 520-1000 | 620-1200
D | >400 | >600 | >800 | >1000 | >1200

## Slide 34: Summary
NRW is a waste of money
Reducing Commercial Losses generates revenue
Reducing Physical Losses reduces the costs of producing the water (chemical and energy reduction)
NRW is a puzzle: analyse and prioritise the approach
Infrastructure Leakage Index (ILI) and Volume of Leakage per Service Connection per Day are international performance indicators of NRW (not %!)