## Slide 1: Leak Detection
Night Flow Measurement, Step Testing, Leak Detection Equipment

## Slide 2: Content
Leakage Components
Leak Detection
Leak Detection Equipment

## Slide 3: Leakage components
Background leakage, bursts

## Slide 4
4
Leakage components
Notes: 4

## Slide 5
5
Background vs burst leakage
Background Leakage
  The aggregation of leakages from all fittings on the distribution network that are too small to be detected by visual or acoustic inspection
    Background leakage are individual leaks with flow rates less than 0.25 m3/hr at 50 m pressure - the minimum leak that can realistically be detected with modern technology
  Major influence: pressure
Burst Leakage
  Loss of water resulting from bursts on the distribution network
  Major influence: the speed with which the burst is located and repaired
  *Amount of water loss through leakage varies during the day as it depends on the pressure
Notes: 5

## Slide 6: 2. Leak detection
Minimum nightflow, step testing

## Slide 7
Minimum Night Flow
Amount of water loss through leakage can be estimated with Minimum Night Flow (MNF) testing
The MNF is the lowest hourly average flow into the DMA over a 24-hour period,
  MNF is usually obtained between 2 and 4am, when most tanks have been filled and users are asleep
The Legitimate Night Flow (LNF) is the customer minimum night consumption at the time of minimum night flow
  Domestic customers – toilet flushing, washing machines etc; use a standard legitimate night time factor, or measured sample
  Large nightly users (such as night clubs or industries) – manually read or log their meter or use a portable meter
The Net Night Flow (NNF) is the DMA leakage at the time of minimum night flow: what remains after subtracting the LNF from the MNF
  Some of the leakage occurs on the customer’s premises and therefore is not part of the utilities NRW. As such, the NNF should be divided into ‘Utility leakage’ and ‘Customer leakage’

## Slide 8
8
Identify the MNF (using a logged DMA meter)
Identify the typical LNF
Calculate the NNF = MNF – LNF
Estimate the ‘Utility leakage’ UNNF = NNF – ‘Customer leakage’
As leakage is proportional to pressure, to represent the average leakage through the day the UNNF should be corrected with a pressure factor (pf), typically pf = average daily DMA pressure / average MNF pressure
Average DMA leakage = UNNF*pf
Minimum Night Flow
Notes: 8

## Slide 9
9
Example
Notes: 9

## Slide 10
10
Step testing
Step testing is a method in which parts of the DMA network are successively isolated to narrow the possible location of leaks
Select the first step furthest away from the DMA water meter
Each step should take around 20 minutes to see the impact
Flow as well as pressure should be checked
Big drop in flow and increasing pressure indicates leakage
Undertake step testing during night time (00.00 – 04.00 am) to avoid measurements disturbed by fluctuations in water demand
First cut off the water supply
Notes: 10

## Slide 11
Step testing example

## Slide 12
Step testing example

## Slide 13
Step testing example

## Slide 14
Step testing example

## Slide 15
Step testing example

## Slide 16
Step testing example

## Slide 17
Step testing example

## Slide 18
Relation flow/pressure and time
Step testing example

## Slide 19: 3. Leak detection equipment
Clamp-on meter, accoustic meter

## Slide 20
Clamp-on meter
A clamp-on meter is a portable meter with which flows can instantaneously be measured through pipes of different types and sizes. Clamp-on meters are used:
When measurements are needed in location where no meters are installed
To check the accuracy of installed meters
Furthermore,
Accuracy of < 1% possible
A clamp-on meter are expensive (~10.000 Euro) and security is needed during night flow measurements
Clamp on meter in box and installed

## Slide 21
Clamp on meter, quick start guide

## Slide 22
Accoustic Meter
Amo

## Slide 23
Other?
Amo